TENDER CLARIFICATION No. 1
Tender Title: To supply, install, test and commission an MRL Traction Passenger Lift at Parish Centre, Xewkija Gozo.
Tender Reference:  02/2026
Contracting Authority: Assoċjazzjoni Rotunda (VO/1867) - Xewkija Parish
Date of Clarification: 4th September 2026

To all prospective bidders

Reference is being made to the above captioned tender for which the deadline for submission of offers is on the 11th September 2026 at noon (12:00pm).

Following a request for clarification received from a prospective tenderer, the Contracting Authority hereby issues the following clarifications for the information and consideration of all prospective tenderers.
The clarifications below shall be read in conjunction with the original tender documents and specifications.

1. Lift Rated Load and Passenger Capacity
Request for Clarification 
“Going through the tender I noticed that the requested rated load of the lift is 450 kg/6 passengers. If the lift is EN 81-70 (new shaft), the capacity should be 630 kg/8 passengers. The dimensions of 1.8 m by 1.8 m should be good to accommodate this.”

Official Clarification
As the Contracting Authority, we hereby confirm that the lift to be supplied under this tender must be fully compliant with the applicable CRPD accessibility requirements.
Accordingly, the minimum internal cabin dimensions, lift door dimensions and all other relevant accessibility requirements shall be in accordance with Section 2.8 and Figure 13 of the Lift Guidelines published as part of the Access for All Guidelines.
Furthermore, based on the applicable European safety standards, namely EN 81-20 and EN 81-70, a lift cabin measuring 1.10 m in width by 1.40 m in depth corresponds to a passenger capacity of 8 persons and a rated load capacity of 630 kg.
In view of the above, the description contained in the tender documents is hereby amended accordingly.
The reference to:
Rated load: 450 kg (6 persons)
shall be read as:
Rated load: 630 kg (8 persons)
Accordingly, the relevant item in the tender documents shall read as follows:
“Supply, deliver, install, test, commission and hand over one (1) complete passenger Machine Room-Less (MRL) lift with a rated load of 630 kg (8 persons), serving 4 stops, complete with 4 automatic entrances, designed to fit within the existing 1.80 m × 1.80 m lift shaft, fully compliant with the Technical Specifications, Drawings, applicable European Standards, CE marking requirements, accessibility requirements (including CRPD compliance), and all applicable legislation. The item shall include all design verification, lift equipment, guide rails, machine and controller, car and landing doors, electrical and mechanical components, wiring, fixings, supports, builder's work in connection, testing, commissioning, statutory inspections, certification, Declaration of Conformity, operation and maintenance manuals, as-built drawings, staff training, warranties, and all labour, materials, plant and equipment necessary to provide a complete, safe and fully operational passenger lift.”
All tenderers shall therefore allow for a 630 kg (8-person) lift when preparing their offers.

2. Lift Travel, Pit Depth and Headroom
Request for Clarification
“Also the lift travel, pit and headroom size are not mentioned.”

Official Clarification
A section through the lift shaft is being made available as part of this clarification.
The dimensions indicated on the drawing are provided for quotation purposes. Tenderers are nevertheless required to verify all dimensions on site and satisfy themselves as to the existing and proposed site conditions before submitting their offer.
The lift shaft has not yet been constructed, although the floor levels are fixed.
The lift pit shall be constructed to a depth of:
1.20 m
Tenderers shall take the above information into consideration when preparing their offers and shall allow for all requirements necessary for the complete installation and commissioning of the lift.

3. Distance Between Power Source and Lift Shaft
Request for Clarification
“We will also need the distance between the power source and the lift shaft.”

Official Clarification
Reference shall be made to the attached drawing, which indicates the relevant information regarding the location of the lift shaft and power source.
Nevertheless, a site visit is deemed necessary, and tenderers are required to verify the actual site conditions and dimensions prior to submitting their offers.
Tenderers shall allow in their offer for all necessary electrical cabling, containment, connections and associated works required for the complete and operational installation of the lift.

4. Lift Car Flooring
Request for Clarification
“If the lift manufacturer sends marble floors (NOT SLIP RESISTANT), the lift would not be in EN 81-70.”

Official Clarification
The preferred lift car flooring is non-slip marble, consisting of marble with an appropriate anti-slip treatment or textured finish, so as to comply with the applicable requirements of EN 81-70.
However, tenderers may alternatively quote for a different flooring material, provided that the proposed material is fully compliant with EN 81-70 and all other applicable accessibility and safety requirements.
Where an alternative flooring material is proposed, the tenderer shall provide full specifications and technical information for the proposed flooring material together with the tender submission, demonstrating its suitability and compliance with the applicable requirements.
The proposed flooring shall be subject to approval by the Contracting Authority/Project Architect or Engineer.

5. Recessed Floor for Subsequent Installation of Marble
Request for Clarification
“We can order you recessed floor and you can install the marble of your choosing afterwards.”

Official Clarification
The provision of a recessed lift car floor to allow the subsequent installation of marble by others is not an option under this tender.
The lift tenderer shall therefore include in its offer the complete and finished lift car flooring in accordance with the requirements specified above.
The flooring provided shall be suitable for the lift installation and shall comply with the applicable requirements of EN 81-70, including the relevant slip-resistance requirements.

Important Notice to All Tenderers

The above clarifications, including the amendment to the rated load from 450 kg (6 persons) to 630 kg (8 persons), shall form an integral part of the tender documentation.
All prospective tenderers shall take these clarifications and amendments into account when preparing and submitting their offers.
Except where expressly amended or clarified above, all other terms, conditions, requirements, specifications and provisions of the original tender documents remain unchanged.
This clarification is being published on the official Xewkija Parish tender website, xewkijaparish.org, and is being made available to all prospective tenderers in order to ensure transparency, equal treatment and a fair tendering process.

Attachments:
1. Lift Section BB DWG.pdf
2. Lift Power Supply Route DWG.pdf
